## Guide
User Guide
1 | 본 문서는 project/proposal 수행 시 Hazardous 관련 유사 information이 필요한 아래의 List를 한 개의 통합 sheet로 관리하기 위해 작성합니다.
a. dHSE (전기) : Hazardouse Source List (Hazardous Area Classification)
b. 건축 : Fire Potential equiment (Fire Proofing)
c. 소방 : F&G (Fire Potential Equipment), Gas Detector
2 | 본 문서 작성시점은 아래와 같습니다. (정확한 시점은 dHSE, 소방 엔지니어와 협의하여 결정)
For Preliminary 송부 - Early work 기간 중
For Final 송부 - Process HAZOP 전
3 | HAZARDOUS SOURCE LIST 작성 관련
a. MATERIAL DESCRIPTION (b열)에 chemical 이름을 'Table 4.4.2' 탭 기준으로 작성
b. 주황색 셀 부분은 NFPA 497의 table 4.4.2 기준으로 자동으로 추가되며, 그 외 data는 개별적으로 작성 필요
4 | HAZARDOUS SUBSTANCE LIST 작성 관련
a. Project spec에 따라 상이한 사항에 대한 부분은 필요여부 및 project 기준을 확인하여 최종 포맷을 Set-up (주황셀, 노란셀)
1) 주황셀 : project requirement에 따라 요구되지 않는 경우에는 삭제 가능
2) 노란셀 : project spec 기준으로 반영하여 작성이 필요함
b. Flash point, AIT는 mixture의 경우 Licensor/FEED에서 주어지지 않았다면, 'substance'에 해당되는 LFL 이상 mol 농도의
single component 중 가장 낮은 flash point로 작성하는 것을 원칙으로 합니다.

## Table 4.4.2
NFPA 497, Table 4.4.2 Selected Chemicals
Chemical | CAS No. | Class I Division Group | Type | Flash Point (℃) | AIT (℃) | % LFL | % UFL | Vapor Density (Air=1) | Vapor Pressure (mmHg) | Class I Zone Group | MIE (mJ) | MIC Ratio | MESG (mm) | Class I Division Group | Check | Class I Zone Group | Check | Type | Check
Acetaldehyde | 75-07-0 | C | I | -38 | 175 | 4 | 60 | 1.5 | 874.9 | IIA | 0.37 | 0.98 | 0.92 | D | Check !! | IIA |  | I
Acetic Acid | 64-19-7 | D | II | 39 | 426 |  | 19.9 | 2.1 | 15.6 | IIA |  | 2.67 | 1.76 | D |  | IIA |  | II
Acetic Acid tert-Butyl Ester | 540-88-5 | D | II |  |  | 1.7 | 9.8 | 4 | 40.6 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Acetic Anhydride | 108-24-7 | D | II | 49 | 316 | 2.7 | 10.3 | 3.5 | 4.9 | IIA |  |  | 1.23 | B | Check !! | IIC | Check !! | II | Check !!
Acetone | 67-64-1 | D | I | -20 | 465 | 2.5 | 12.8 | 2 | 230.7 | IIA | 1.15 | 1 | 1.02 | D |  | IIA |  | I
Acetone Cyanohydrin | 75-86-5 | D | IIIA | 74 | 688 | 2.2 | 12 | 2.9 | 0.3 |  |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Acetonitrile | 75-05-08 | D | I | 6 | 524 | 3 | 16 | 1.4 | 91.1 | IIA | 1.5 |  |  | B | Check !! | IIC | Check !! | I | Check !!
Acetylene | 74-86-2 | A | GAS |  | 305 | 2.5 | 100 | 0.9 | 36600 | IIC | 0.017 | 0.28 | 0.25 | A |  | IIC |  | I
Acrolein (Inhibited) | 107-02-8 | B,C | I |  | 235 | 2.8 | 31 | 1.9 | 274.1 | IIB | 0.13 |  |  | B | Check !! | IIC | Check !! | I | Check !!
Acrylic Acid | 79-10-07 | D | II | 54 | 438 | 2.4 | 8 | 2.5 | 4.3 | IIB |  |  | 0.86 | B | Check !! | IIC | Check !! | II | Check !!
Acrylonitrile | 107-13-1 | D | I | 0 | 481 | 3 | 17 | 1.8 | 108.5 | IIB | 0.16 | 0.78 | 0.87 | C | Check !! | IIB |  | I
Adiponitrile | 111-69-3 | D | IIIA | 93 | 550 |  |  | 1 | 0.002 |  |  |  |  | B | Check !! | IIC | Check !! | IIIB | Check !!
Allyl Alcohol | 107-18-6 | C | I | 22 | 378 | 2.5 | 18 | 2 | 25.4 | IIB |  |  | 0.84 | B | Check !! | IIC | Check !! | I | Check !!
Allyl Chloride | 107-05-1 | D | I | -32 | 485 | 2.9 | 11.1 | 2.6 | 366 | IIA |  | 1.33 | 1.17 | D |  | IIA |  | I
Allyl Glycidyl Ether | 106-92-3 | B | II |  | 57 |  |  | 3.9 | [5 empty] | B |  | IIC | Check !! | I | Check !!
Alpha-Methyl Styrene | 98-83-9 | D | II |  | 574 | 0.8 | 11 | 4.1 | 2.7 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
n-Amyl Acetate | 628-63-7 | D | I | 25 | 360 | 1.1 | 7.5 | 4.5 | 4.2 | IIA |  |  | 1.02 | B | Check !! | IIC | Check !! | I | Check !!
sec-Amyl Acetate | 626-38-0 | D | I | 23 |  | 1.1 | 7.5 | 4.5 |  | IIA |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Ammonia | 7664-41-7 | D | GAS |  | 651 | 15 | 28 | 0.6 | 7498 | IIA | 680 | 6.85 | 3.17 | D |  | IIA |  | I
Aniline | 62-53-3 | D | IIIA | 70 | 615 | 1.2 | 8.3 | 3.2 | 0.7 | IIA |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Benzene | 71-43-2 | D | I | -11 | 498 | 1.2 | 7.8 | 2.8 | 94.8 | IIA | 0.2 | 1 | 0.99 | D |  | IIA |  | I
Benzyl Chloride | 98-87-3 | D | IIIA |  | 585 | 1.1 |  | 4.4 | 0.5 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Bromopropyne | 106-96-7 | D | I | 10 | 324 | 3 | [7 empty] | B | Check !! | IIC | Check !! | I | Check !!
n-Butane | 106-97-8 | D | GAS |  | 288 | 1.9 | 8.5 | 2 |  | IIA | 0.25 | 0.94 | 1.07 | D |  | IIA |  | I
1,3-Butadiene | 106-99-0 | B,D | GAS |  | 420 | 2 | 11.5 | 1.9 |  | IIB | 0.13 | 0.76 | 0.79 | C | Check !! | IIB |  | I
1-Butanol | 71-36-3 | D | I | 36 | 343 | 1.4 | 11.2 | 2.6 | 7 | IIA |  |  | 0.91 | B | Check !! | IIC | Check !! | I | Check !!
Butyl alcohol (s) (butanol-2) | 78-92-2 | D | I | 23.8 | 405 | 1.7 | 9.8 | 2.6 |  | IIA |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Butylamine | 109-73-9 | D | GAS | -12 | 312 | 1.7 | 9.8 | 2.5 | 92.9 | IIA |  | 1.13 |  | B | Check !! | IIC | Check !! | I | Check !!
Butylene | 25167-67-3 | D | I |  | 385 | 1.6 | 10 | 1.9 | 2214.6 | IIA |  |  | 0.94 | B | Check !! | IIC | Check !! | I | Check !!
n-Butyraldehyde | 123-72-8 | C | I | -12 | 218 | 1.9 | 12.5 | 2.5 | 112.2 | IIA |  |  | 0.92 | B | Check !! | IIC | Check !! | I | Check !!
n-Butyl Acetate | 123-86-4 | D | I | 22 | 421 | 1.7 | 7.6 | 4 | 11.5 | IIA |  | 1.08 | 1.04 | D |  | IIA |  | I
sec-Butyl Acetate | 105-46-4 | D | II | -8 |  | 1.7 | 9.8 | 4 | 22.2 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
tert-Butyl Acrylate | 540-88-5 | D | II |  |  | 1.7 | 9.8 | 4 | 40.6 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
n-Butyl Acrylate (Inhibited) | 141-32-2 | D | II | 49 | 293 | 1.7 | 9.9 | 4.4 | 5.5 | IIB |  |  | 0.88 | B | Check !! | IIC | Check !! | II | Check !!
n-Butyl Glycidyl Ether | 2426-08-06 | B,C | II | [10 empty] | B | Check !! | IIC | Check !! | I | Check !!
n-Butyl Formal | 110-62-3 | C | IIIA | [5 empty] | 34.3 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Butyl Mercaptan | 109-79-5 | C | I | 2 |  |  |  | 3.1 | 46.4 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Butyl-2-Propenoate | 141-32-2 | D | II | 49 |  | 1.7 | 9.9 | 4.4 | 5.5 |  |  |  |  | B | Check !! | IIC | Check !! | II | Check !!
para tert-Butyl Toluene | 98-51-1 | D | IIIA | [10 empty] | B | Check !! | IIC | Check !! | I | Check !!
n-Butyric Acid | 107-92-6 | D | IIIA | 72 | 443 | 2 | 10 | 3 | 0.8 |  |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Carbon Disulfide | 75-15-0 |  | I | -30 | 90 | 1.3 | 50 | 2.6 | 358.8 | IIC | 0.009 | 0.39 | 0.2 | B | Check !! | IIC |  | I
Carbon Monoxide | 630-08-0 | C | GAS |  | 609 | 12.5 | 74 | 0.97 |  | IIB | 0.54 |  |  | B | Check !! | IIC | Check !! | I | Check !!
Chloroacetaldehyde | 107-20-0 | C | IIIA | 88 |  |  |  |  | 63.1 |  |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Chlorobenzene | 108-90-7 | D | I | 29 | 593 | 1.3 | 9.6 | 3.9 | 11.9 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
1-Chloro-1- Nitropropane | 2425-66-3 | C | IIIA | [10 empty] | B | Check !! | IIC | Check !! | I | Check !!
Chloroprene | 126-99-8 | D | GAS | -20 |  | 4 | 20 | 3 | [5 empty] | B | Check !! | IIC | Check !! | I | Check !!
Cresol | 1319-77-3 | D | IIIA | 81 | 559 | 1.1 |  | 3.7 | [5 empty] | B | Check !! | IIC | Check !! | IIIA | Check !!
Crotonaldehyde | 4170-30-3 | C | I | 13 | 232 | 2.1 | 15.5 | 2.4 | 33.1 | IIB |  |  | 0.81 | B | Check !! | IIC | Check !! | I | Check !!
Cumene | 98-82-8 | D | I | 36 | 424 | 0.9 | 6.5 | 4.1 | 4.6 | IIA |  |  | 1.05 | B | Check !! | IIC | Check !! | I | Check !!
Cyclohexane | 110-82-7 | D | I | -17 | 245 | 1.3 | 8 | 2.9 | 98.8 | IIA | 0.22 | 1 | 0.94 | D |  | IIA |  | I
Cyclohexanol | 108-93-0 | D | IIIA | 68 | 300 |  |  | 3.5 | 0.7 | IIA |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Cyclohexanone | 108-94-1 | D | II | 44 | 420 | 1.1 | 9.4 | 3.4 | 4.3 | IIA |  |  | 0.98 | B | Check !! | IIC | Check !! | II | Check !!
Cyclohexene | 110-83-8 | D | I | -6 | 244 | 1.2 |  | 2.8 | 89.4 | IIA |  | 0.97 |  | B | Check !! | IIC | Check !! | I | Check !!
Cyclopropane | 75-19-4 | D | I |  | 503 | 2.4 | 10.4 | 1.5 | 5430 | IIA | 0.17 | 0.84 | 0.91 | D |  | IIA |  | I
p-Cymene | 99-87-6 | D | II | 47 | 436 | 0.7 | 5.6 | 4.6 | 1.5 | IIA |  |  |  | B | Check !! | IIC | Check !! | II | Check !!
Decene | 872-05-9 | D | II |  | 235 |  |  | 4.8 | 1.7 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
n-Decaldehyde | 112-31-2 | C | IIIA | [5 empty] | 0.09 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
n-Decanol | 112-30-1 | D | IIIA | 82 | 288 |  |  | 5.3 | 0.008 |  |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Decyl Alcohol | 112-30-1 | D | IIIA | 82 | 288 |  |  | 5.3 | 0.008 |  |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Diacetone Alcohol | 123-42-2 | D | IIIA | 64 | 603 | 1.8 | 6.9 | 4 | 1.4 |  |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Di-Isobutylene | 25167-70-8 | D | I | 2 | 391 | 0.8 | 4.8 | 3.8 |  |  | 0.96 |  |  | B | Check !! | IIC | Check !! | I | Check !!
Di-Isobutyl Ketone | 108-83-8 | D | II | 60 | 396 | 0.8 | 7.1 | 4.9 | 1.7 |  |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
o-Dichlorobenzene | 955-50-1 | D | IIIA | 66 | 647 | 2.2 | 9.2 | 5.1 |  | IIA |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
1,4-Dichloro-2,3 Epoxybutane | 3583-47-9 | D | I |  |  | 1.9 | 8.5 | 2 |  | IIA | 0.25 | 0.98 | 1.07 | D |  | IIA |  | I
1,1-Dichloroethane | 1300-21-6 | D | I |  | 438 | 6.2 | 16 | 3.4 | 227 | IIA |  |  | 1.82 | B | Check !! | IIC | Check !! | I | Check !!
1,2-Dichloroethylene | 156-59-2 | D | I | 97 | 460 | 5.6 | 12.8 | 3.4 | 204 | IIA |  |  | 3.91 | B | Check !! | IIC | Check !! | IIIB | Check !!
1,1-Dichloro-1-Nitroethane | 594-72-9 | C | IIIA | 76 |  |  |  | 5 | [5 empty] | B | Check !! | IIC | Check !! | IIIA | Check !!
1,3-Dichloropropene | 10061-02-6 | D | I | 35 |  | 5.3 | 14.5 | 3.8 | [5 empty] | B | Check !! | IIC | Check !! | I | Check !!
Dicyclopentadiene | 77-73-6 | C | I | 32 | 503 |  |  |  | 2.8 | IIA |  |  | 0.91 | B | Check !! | IIC | Check !! | I | Check !!
Diethylamine | 109-87-9 | C | I | -28 | 312 | 1.8 | 10.1 | 2.5 |  | IIA |  |  | 1.15 | B | Check !! | IIC | Check !! | I | Check !!
Diethylaminoethanol | 100-37-8 | C | IIIA | 60 | 320 |  |  | 4 | 1.6 | IIA |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Diethyl Benzene | 25340-17-4 | D | II | 57 | 395 |  |  | 4.6 | [5 empty] | B | Check !! | IIC | Check !! | II | Check !!
Diethyl Ether (Ethyl Ether) | 60-29-7 | C | I | -45 | 160 | 1.9 | 36 | 2.6 | 538 | IIB | 0.19 | 0.88 | 0.83 | D | Check !! | IIB |  | I
Diethylene Glycol Monobutyl Ether | 112-34-5 | C | IIIA | 78 | 228 | 0.9 | 24.6 | 5.6 | 0.02 |  |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Diethylene Glycol Monomethyl Ether | 111-77-3 | C | IIIA | 93 | 241 |  |  |  | 0.2 |  |  |  |  | B | Check !! | IIC | Check !! | IIIB | Check !!
n-n-Dimethyl Aniline | 121-69-7 | C | IIIA | 63 | 371 | 1 |  | 4.2 | 0.7 |  |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Dimethyl Formamide | 68-12-02 | D | II | 58 | 455 | 2.2 | 15.2 | 2.5 | 4.1 | IIA |  |  | 1.08 | B | Check !! | IIC | Check !! | II | Check !!
Dimethyl Sulfate | 77-78-1 | D | IIIA | 83 | 188 |  |  | 4.4 | 0.7 |  |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Dimethylamine | 124-40-3 | C | GAS |  | 400 | 2.8 | 14.4 | 1.6 |  | IIA |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
2,2-Dimethylbutane | 75-83-2 | D | I | -48 | 405 |  |  |  | 319.3 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
2,3-Dimethylbutane | 78-29-8 | D | I |  | 396 | [8 empty] | B | Check !! | IIC | Check !! | I | Check !!
3,3-Dimethylheptane | 1071-26-7 | D | I |  | 325 |  |  |  | 10.8 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
2,3-Dimethylhexane | 31394-54-4 | D | I |  | 438 | [8 empty] | B | Check !! | IIC | Check !! | I | Check !!
2,3-Dimethylpentane | 107-83-5 | D | I |  | 335 |  |  |  | 211.7 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Di-N-Propylamine | 142-84-7 | C | I | 17 | 299 |  |  |  | 27.1 | IIA |  |  | 0.95 | B | Check !! | IIC | Check !! | I | Check !!
1,4-Dioxane | 123-91-1 | C | I | 12 | 180 | 2 | 22 | 3 | 38.2 | IIB | 0.19 |  | 0.7 | B | Check !! | IIC | Check !! | I | Check !!
Dipentene | 138-86-3 | D | II | 45 | 237 | 0.7 | 6.1 | 4.7 |  | IIA |  |  | 1.18 | B | Check !! | IIC | Check !! | II | Check !!
Dipropylene Glycol Methyl Ether | 34590-94-8 | C | IIIA | 85 |  | 1.1 | 3 | 5.1 | 0.5 |  |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Diisopropylamine | 108-18-9 | C | GAS | ?6 | 316 | 1.1 | 7.1 | 3.5 |  | IIA |  |  | 1.02 | B | Check !! | IIC | Check !! | IIIB | Check !!
Dodecene | 6842-15-5 | D | IIIA | 100 | 255 | [8 empty] | B | Check !! | IIC | Check !! | IIIB | Check !!
Epichlorohydrin | 3132-64-7 | C | I | 33 | 411 | 3.8 | 21 | 3.2 | 13 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Ethane | 74-84-0 | D | GAS | -29 | 472 | 3 | 12.5 | 1 |  | IIA | 0.24 | 0.82 | 0.91 | D |  | IIA |  | I
Ethanol | 64-17-5 | D | I | 13 | 363 | 3.3 | 19 | 1.6 | 59.5 | IIA |  | 0.88 | 0.89 | D |  | IIB | Check !! | I | Check !!
Ethylamine | 1975-04-07 | D | I | -18 | 385 | 3.5 | 14 | 1.6 | 1048 |  | 2.4 |  |  | B | Check !! | IIC | Check !! | I | Check !!
Ethylene | 74-85-1 | C | GAS |  | 490 | 2.7 | 36 | 1 |  | IIB | 0.07 | 0.53 | 0.65 | C |  | IIB |  | I
Ethylenediamine | 107-15-3 | D | I | 33 | 385 | 2.5 | 12 | 2.1 | 12.5 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Ethylenimine | 151-56-4 | C | I | -11 | 320 | 3.3 | 54.8 | 1.5 | 211 |  | 0.48 |  |  | B | Check !! | IIC | Check !! | I | Check !!
Ethylene Chlorohydrin | 107-07-3 | D | IIIA | 59 | 425 | 4.9 | 15.9 | 2.8 | 7.2 |  |  |  |  | B | Check !! | IIC | Check !! | II | Check !!
Ethylene Dichloride | 107-06-2 | D | I | 13 | 413 | 6.2 | 16 | 3.4 | 79.7 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Ethylene Glycol Monoethyl Ether Acetate | 111-15-9 | C | II | 47 | 379 | 1.7 | 4.7 | 2.3 |  | IIA |  | 0.53 | 0.97 | C |  | IIB | Check !! | II | Check !!
Ethylene Glycol Monobutyl Ether Acetate | 112-07-2 | C | IIIA |  | 340 | 0.9 | 8.5 |  | 0.9 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Ethylene Glycol Monobutyl Ether | 111-76-2 | C | IIIA |  | 238 | 1.1 | 12.7 | 4.1 | 1 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Ethylene Glycol Monoethyl Ether | 110-80-5 | C | II |  | 235 | 1.7 | 15.6 | 3 | 5.4 |  |  |  | 0.84 | B | Check !! | IIC | Check !! | I | Check !!
Ethylene Glycol Monomethyl Ether | 109-86-4 | D | II |  | 285 | 1.8 | 14 | 2.6 | 9.2 |  |  |  | 0.85 | B | Check !! | IIC | Check !! | I | Check !!
Ethylene Oxide | 75-21-8 | B,C | I | -20 | 429 | 3 | 100 | 1.5 | 1314 | IIB | 0.065 | 0.47 | 0.59 | C | Check !! | IIB |  | I
2-Ethylhexaldehyde | 123-05-7 | C | II | 52 | 191 | 0.8 | 7.2 | 4.4 | 1.9 |  |  |  |  | B | Check !! | IIC | Check !! | II | Check !!
2-Ethylhexanol | 104-76-7 | D | IIIA | 81 |  | 0.9 | 9.7 | 4.5 | 0.2 |  |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
2-Ethylhexyl Acrylate | 103-09-3 | D | IIIA | 88 | 252 |  |  |  | 0.3 |  |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Ethyl Acetate | 141-78-6 | D | I | -4 | 427 | 2 | 11.5 | 3 | 93.2 | IIA | 0.46 |  | 0.99 | B | Check !! | IIC | Check !! | I | Check !!
Ethyl Acrylate (Inhibited) | 140-88-5 | D | I | 9 | 372 | 1.4 | 14 | 3.5 | 37.5 | IIA |  |  | 0.86 | B | Check !! | IIC | Check !! | I | Check !!
Ethyl Alcohol | 64-17-5 | D | I | 13 | 363 | 3.3 | 19 | 1.6 | 59.5 | IIA |  | 0.88 | 0.89 | D |  | IIB | Check !! | I | Check !!
Ethyl Sec-Amyl Ketone | 541-85-5 | D | II | 59 | [9 empty] | B | Check !! | IIC | Check !! | II | Check !!
Ethyl Benzene | 100-41-4 | D | I | 15 | 432 | 0.8 | 6.7 | 3.7 | 9.6 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Ethyl Butanol | 97-95-0 | D | II | 57 |  | 1.2 | 7.7 | 3.5 | 1.5 |  |  |  |  | B | Check !! | IIC | Check !! | II | Check !!
Ethyl Butyl Ketone | 106-35-4 | D | II | 46 |  |  |  | 4 | 3.6 |  |  |  |  | B | Check !! | IIC | Check !! | II | Check !!
Ethyl Chloride | 75-00-3 | D | GAS | ?50 | 519 | 3.8 | 15.4 | 2.2 | [5 empty] | B | Check !! | IIC | Check !! | IIIB | Check !!
Ethyl Formate | 109-94-4 | D | GAS | ?20 | 455 | 2.8 | 16 | 2.6 | IIA | 0.94 |  |  |  | B | Check !! | IIC | Check !! | IIIB | Check !!
Ethyl Mercaptan | 75-08-01 | C | I | ?18 | 300 | 2.8 | 18 | 2.1 | 527.4 | IIB | 0.9 | 0.9 |  | B | Check !! | IIC | Check !! | IIIB | Check !!
n-Ethyl Morpholine | 100-74-3 | C | I | 32 | 4 | [8 empty] | B | Check !! | IIC | Check !! | I | Check !!
2-Ethyl-3-Propyl Acrolein | 645-62-5 | C | IIIA | 68 | 4.4 | [8 empty] | B | Check !! | IIC | Check !! | IIIA | Check !!
Ethyl Silicate | 78-10-04 | D | II | 7.2 | [9 empty] | B | Check !! | IIC | Check !! | I | Check !!
Formaldehyde (Gas) | 50-00-0 | B | GAS | 430 | 7 | 73 | 1 | IIB | 0.57 |  |  |  |  | B |  | IIC | Check !! | IIIB | Check !!
Formic Acid | 64-18-6 | D | II | 50 | 434 | 18 | 57 | 1.6 | 42.7 | IIA | 1.86 |  |  | B | Check !! | IIC | Check !! | II | Check !!
Fuel Oil 1 | 8008-20-6 | D | II or IIIA | 38~72k | 210 | 0.7 | 5 | [6 empty] | B | Check !! | IIC | Check !! | IIIB | Check !!
Fuel Oil 2 |  |  | II or IIIA | 52~96k | 257 | [8 empty] | B | Check !! | IIC | Check !! | IIIB | Check !!
Fuel Oil 6 |  |  | IIIA or IIIB | 66~132k | [9 empty] | B | Check !! | IIC | Check !! | IIIB | Check !!
Furfural | 98-01-01 | C | IIIA | 60 | 316 | 2.1 | 19.3 | 3.3 | 2.3 |  |  |  | 0.94 | B | Check !! | IIC | Check !! | IIIA | Check !!
Furfuryl Alcohol | 98-00-0 | C | IIIA | 75 | 490 | 1.8 | 16.3 | 3.4 | 0.6 |  |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Gasoline | 8006-61-9 | D | I | -46 | 280 | 1.4 | 7.6 | 3 | [5 empty] | B | Check !! | IIC | Check !! | I | Check !!
n-Heptane | 142-82-5 | D | I | -4 | 204 | 1 | 6.7 | 3.5 | 45.5 | IIA | 0.24 | 0.88 | 0.91 | D |  | IIA |  | I
n-Heptene | 81624-04-6 | D | I | -1 | 204 |  |  |  | 3.4 |  |  |  | 0.97 | B | Check !! | IIC | Check !! | I | Check !!
n-Hexane | 110-54-3 | D | I | -23 | 225 | 1.1 | 7.5 | 3 | 152 | IIA | 0.24 | 0.88 | 0.93 | D |  | IIA |  | I
Hexanol | 111-27-3 | D | IIIA | 63 |  |  |  | 3.5 | 0.8 | IIA |  |  | 0.98 | B | Check !! | IIC | Check !! | IIIA | Check !!
2-Hexanone | 591-78-6 | D | I | 35 | 424 | 1.2 | 8 | 3.5 | 10.6 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Hexene | 592-41-6 | D | I | -26 | 245 | 1.2 | 6.9 |  | 186 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
sec-Hexyl Acetate | 108-84-9 | D | II | 45 | 5 | [8 empty] | B | Check !! | IIC | Check !! | II | Check !!
Hydrazine | 302-01-2 | C | II | 38 | 23 |  | 98 | 1.1 | 14.4 |  |  |  |  | B | Check !! | IIC | Check !! | II | Check !!
Hydrogen | 1333-74-0 | B | GAS |  | 500 | 4 | 75 | 0.1 |  | IIC | 0.019 | 0.25 | 0.28 | B |  | IIC |  | I
Hydrogen Cyanide | 74-90-8 | C | GAS | -18 | 538 | 5.6 | 40 | 0.9 |  | IIB |  |  | 0.8 | B | Check !! | IIC | Check !! | I | Check !!
Hydrogen Selenide | 2148909 | C | I | [5 empty] | 7793 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Hydrogen Sulfide | 2148878 | C | GAS |  | 260 | 4 | 44 | 1.2 |  | IIB | 0.068 |  | 0.9 | B | Check !! | IIC | Check !! | I | Check !!
Isoamyl Acetate | 123-92-2 | D | I | 25 | 360 | 1 | 7.5 | 4.5 | 6.1 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Isoamyl Alcohol | 123-51-3 | D | II | 43 | 350 | 1.2 | 9 | 3 | 3.2 | IIA |  |  | 1.02 | B | Check !! | IIC | Check !! | II | Check !!
Isobutane | 75-28-5 | D | GAS |  | 460 | 1.8 | 8.4 | 2 |  | IIA |  |  | 0.95 | B | Check !! | IIC | Check !! | I | Check !!
Isobutyl Acetate | 110-19-0 | D | I | 18 | 421 | 2.4 | 10.5 | 4 | 17.8 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Isobutyl Acrylate | 106-63-8 | D | I |  | 427 |  |  | 4.4 | 7.1 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Isobutyl Alcohol | 78-83-1 | D | I | -40 | 416 | 1.2 | 10.9 | 2.5 | 10.5 | IIA |  | 0.92 | 0.98 | D |  | IIA |  | I
Isobutyraldehyde | 78-84-2 | C | GAS | -40 | 196 | 1.6 | 10.6 | 2.5 |  | IIA |  |  | 0.92 | B | Check !! | IIC | Check !! | I | Check !!
Isodecaldehyde | 112-31-2 | C | IIIA |  |  |  |  | 5.4 | 0.09 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Isohexane | 107-83-5 | D |  |  | 264 |  |  |  | 211.7 | IIA |  | 1 |  | B | Check !! | IIC | Check !! | I | Check !!
Isopentane | 78-78-4 | D |  |  | 420 |  |  |  | 688.6 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Isooctyl Aldehyde | 123-05-7 | C | II |  | 197 |  |  |  | 1.9 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Isophorone | 78-59-1 | D |  | 84 | 460 | 0.8 | 3.8 | 4.8 | 0.4 |  |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Isoprene | 78-79-5 | D | I | -54 | 220 | 1.5 | 8.9 | 2.4 | 550.6 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Isopropyl Acetate | 108-21-4 | D | I |  | 460 | 1.8 | 8 | 3.5 | 60.4 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Isopropyl Ether | 108-20-3 | D | I | -28 | 443 | 1.4 | 7.9 | 3.5 | 148.7 | IIA |  |  | 0.94 | B | Check !! | IIC | Check !! | I | Check !!
Isopropyl Glycidyl Ether | 4016-14-2 | C | I | [10 empty] | B | Check !! | IIC | Check !! | I | Check !!
Isopropylamine | 75-31-0 | D | GAS | -26 | 402 | 2.3 | 10.4 | 2 |  |  | 2 |  |  | B | Check !! | IIC | Check !! | I | Check !!
Kerosene | 8008-20-6 | D | II | 72 | 210 | 0.7 | 5 |  |  | IIA |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Liquefied Petroleum Gas | 68476-85-7 | D | I |  | 405 | [8 empty] | B | Check !! | IIC | Check !! | I | Check !!
Mesityl Oxide | 141-97-9 | D | I | 31 | 344 | 1.4 | 7.2 | 3.4 | 47.6 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Methane | 74-82-8 | D | GAS |  | 600 | 5 | 15 | 0.6 |  | IIA | 0.28 | 1 | 1.12 | D |  | IIA |  | I
Methanol | 67-56-1 | D | I | 12 | 385 | 6 | 36 | 1.1 | 126.3 | IIA | 0.14 | 0.82 | 0.92 | D |  | IIA |  | I
Methyl Acetate | 79-20-9 | D | GAS | -10 | 454 | 3.1 | 16 | 2.6 |  | IIA |  | 1.08 | 0.99 | D |  | IIA |  | I
Methyl Acrylate | 96-33-3 | D | GAS | -3 | 468 | 2.8 | 25 | 3 |  | IIB |  | 0.98 | 0.85 | D |  | IIB |  | I
Methyl Alcohol | 67-56-1 | D | I |  | 385 | 6 | 36 | 1.1 | 126.3 | IIA |  |  | 0.91 | B | Check !! | IIC | Check !! | I | Check !!
Methyl Amyl Alchol | 108-11-2 | D | II | 41 |  | 1 | 5.5 | 3.5 | 5.3 | IIA |  |  | 1.01 | B | Check !! | IIC | Check !! | II | Check !!
Methyl Chloride | 74-87-3 | D | GAS | -46 | 632 | 8.1 | 17.4 | 1.7 |  | IIA |  |  | 1 | B | Check !! | IIC | Check !! | I | Check !!
Methyl Ether | 115-10-6 | C | GAS | -41 | 350 | 3.4 | 27 | 1.6 |  | IIB |  | 0.85 | 0.84 | D | Check !! | IIB |  | I
Methyl Ethyl Ketone | 78-93-3 | D | I | -6 | 404 | 1.4 | 11.4 | 2.5 | 92.4 | IIB | 0.53 | 0.92 | 0.84 | D |  | IIB |  | I
Methyl Formal | 534-15-6 | C | I | 1 | 238 |  |  | 3.1 | [5 empty] | B | Check !! | IIC | Check !! | I | Check !!
Methyl Formate | 107-31-3 | D | GAS | -19 | 449 | 4.5 | 23 | 2.1 |  | IIA |  |  | 0.94 | B | Check !! | IIC | Check !! | I | Check !!
2-Methylhexane | 31394-54-4 | D | I |  | 280 | [8 empty] | B | Check !! | IIC | Check !! | I | Check !!
Methyl Isobutyl Ketone | 108-10-1 | D | I | 13 | 440 | 1.2 | 8 | 3.5 | 11 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Methyl Isocyanate | 624-83-9 | D | GAS | -15 | 534 | 5.3 | 26 | 2 |  | IIA |  |  | 1.21 | B | Check !! | IIC | Check !! | I | Check !!
Methyl Mercaptan | 74-93-1 | C | GAS | -18 |  | 3.9 | 21.8 | 1.7 | [5 empty] | B | Check !! | IIC | Check !! | I | Check !!
Methyl Methacrylate | 80-62-6 | D | I | 10 | 422 | 1.7 | 8.2 | 3.6 | 37.2 | IIA |  |  | 0.95 | B | Check !! | IIC | Check !! | I | Check !!
Methyl N-Amyl Ketone | 110-43-0 | D | II | 49 | 393 | 1.1 | 7.9 | 3.9 | 3.8 |  |  |  |  | B | Check !! | IIC | Check !! | II | Check !!
Methyl Tertiary Butyl Ether | 1634-04-4 | D | I | -80 | 435 | 1.6 | 8.4 | 0.2 | 250.1 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
2-Methyloctane | 3221-61-2 |  |  |  | 220 |  |  |  | 6.3 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
2-Methylpropane | 75-28-5 | D | I | 460 | 2639 | [8 empty] | B | Check !! | IIC | Check !! | IIIB | Check !!
Methyl-1-Propanol | 78-83-1 | D | I | ?40 | 416 | 1.2 | 10.9 | 2.5 | 10.1 | IIA | 0.98 |  |  | B | Check !! | IIC | Check !! | IIIB | Check !!
Methyl-2-Propanol | 75-65-0 | D | I | 10 | 360 | 2.4 | 8 | 2.6 | 42.2 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
2-Methyl-5-Ethyl Pyridine | 104-90-5 | D |  | 74 |  | 1.1 | 6.6 | 4.2 | [5 empty] | B | Check !! | IIC | Check !! | IIIA | Check !!
Methylacetylene | 74-99-7 | C | I |  |  | 1.7 |  | 1.4 | 4306 |  | 0.11 |  |  | B | Check !! | IIC | Check !! | I | Check !!
Methylacetylene-Propadiene | 27846-30-6 |  | I | [6 empty] | IIB |  |  | 0.74 | B | Check !! | IIC | Check !! | I | Check !!
Methylal | 109-87-5 | C | I | -18 | 237 | 1.6 | 17.6 | 2.6 | 398 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Methylamine | 74-89-5 | D | GAS |  | 430 | 4.9 | 20.7 | 1 |  | IIA |  |  | 1.1 | B | Check !! | IIC | Check !! | I | Check !!
2-Methylbutane | 78-78-4 | D |  | -56 | 420 | 1.4 | 8.3 | 2.6 | 688.6 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Methylcyclohexane | 208-87-2 | D | I | -4 | 250 | 1.2 | 6.7 | 3.4 |  |  | 0.27 |  |  | B | Check !! | IIC | Check !! | I | Check !!
Methylcyclohexanol | 25630-42-3 | D |  | 68 | 296 |  |  | 3.9 | [5 empty] | B | Check !! | IIC | Check !! | IIIA | Check !!
2-Methycyclohexanone | 583-60-8 | D | II |  |  |  |  | 3.9 | [5 empty] | B | Check !! | IIC | Check !! | I | Check !!
2-Methylheptane |  | D |  |  | 420 | [8 empty] | B | Check !! | IIC | Check !! | I | Check !!
3-Methylhexane | 589-34-4 | D |  |  | 280 |  |  |  | 61.5 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
3-Methylpentane | 94-14-0 | D |  |  | 278 | [8 empty] | B | Check !! | IIC | Check !! | I | Check !!
2-Methylpropane | 75-28-5 | D | I |  | 460 |  |  |  | 2639 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
2-Methyl-1-Propanol | 78-83-1 | D | I | -40 | 223 | 1.2 | 10.9 | 2.5 | 10.5 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
2-Methyl-2-Propanol | 75-65-0 | D | I |  | 478 | 2.4 | 8 | 2.6 | 42.2 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
2-Methyloctane | 2216-32-2 | D |  |  | 220 | [8 empty] | B | Check !! | IIC | Check !! | I | Check !!
3-Methyloctane | 2216-33-3 | D |  |  | 220 |  |  |  | 6.3 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
4-Methyloctane | 2216-34-4 | D |  |  | 225 |  |  |  | 6.8 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Monoethanolamine | 141-43-5 | D |  | 85 | 410 |  |  | 2.1 | 0.4 | IIA |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Monoisopropanolamine | 78-96-6 | C | D | 77 | 374 |  |  | 2.6 | 1.1 |  |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Monomethyl Aniline | 100-61-8 | C |  |  | 482 |  |  |  | 0.5 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Monomethyl Hydrazine | 60-34-4 | C | I | 23 | 194 | 2.5 | 92 | 1.6 | [5 empty] | B | Check !! | IIC | Check !! | I | Check !!
Morpholine | 110-91-8 | C | II | 35 | 310 | 1.4 | 11.2 | 3 | 10.1 | IIA |  |  | 0.95 | B | Check !! | IIC | Check !! | I | Check !!
Naphtha (Coal Tar) | 8030-30-6 | D | II | 42 | 277 |  |  |  |  | IIA |  |  |  | B | Check !! | IIC | Check !! | II | Check !!
Naphtha (Petroleum) | 8030-30-6 | D | I | 42 | 288 | 1.1 | 5.9 | 2.5 |  | IIA |  |  |  | B | Check !! | IIC | Check !! | II | Check !!
Neopentane | 463-82-1 | D |  | -65 | 450 | 1.4 | 8.3 | 2.6 | 1286 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Nitrobenzene | 98-95-3 | D |  | 88 | 482 | 1.8 |  | 4.3 | 0.3 | IIA |  |  | 0.94 | B | Check !! | IIC | Check !! | IIIA | Check !!
Nitroethane | 79-24-3 | C | I | 28 | 414 | 3.4 |  | 2.6 | 20.7 | IIB |  |  | 0.87 | B | Check !! | IIC | Check !! | I | Check !!
Nitromethane | 75-52-5 | C | I | 35 | 418 | 7.3 |  | 2.1 | 36.1 | IIA |  | 0.92 | 1.17 | D | Check !! | IIA |  | I
1-Nitropropane | 108-03-2 | C | I | 34 | 421 | 2.2 |  | 3.1 | 10.1 | IIB |  |  | 0.84 | B | Check !! | IIC | Check !! | I | Check !!
2-Nitropropane | 79-46-9 | C | I | 28 | 428 | 2.6 | 11 | 3.1 | 17.1 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
n-Nonane | 111-84-2 | D | I | 31 | 205 | 0.8 | 2.9 | 4.4 | 4.4 | IIA |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Nonene | 27214-95-8 | D | I |  |  | 0.8 |  | 4.4 | [5 empty] | B | Check !! | IIC | Check !! | I | Check !!
Nonyl Alcohol | 143-08-8 | D |  |  |  | 0.8 | 6.1 | 5 | 0.02 | IIA |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
n-Octane | 111-65-9 | D | I | 13 | 206 | 1 | 6.5 | 3.9 | 14 | IIA | 0.94 |  |  | B | Check !! | IIC | Check !! | I | Check !!
Octene | 25377-83-7 | D | I | 8 | 230 | 0.9 |  | 3.9 | [5 empty] | B | Check !! | IIC | Check !! | I | Check !!
n-Octyl Alcohol | 111-87-5 | D | [5 empty] | 4.5 | 0.08 | IIA | 1.05 |  |  | B | Check !! | IIC | Check !! | I | Check !!
n-Pentane | 109-66-0 | D | I | -40 | 243 | 1.5 | 7.8 | 2.5 | 513 | IIA | 0.28 | 0.97 |  | B | Check !! | IIC | Check !! | I | Check !!
1-Pentanol | 71-41-0 | D | I | 33 | 300 | 1.2 | 10 | 3 | 2.5 | IIA | 1.3 |  |  | B | Check !! | IIC | Check !! | I | Check !!
2-Pentanone | 107-87-9 | D | I | 7 | 452 | 1.5 | 8.2 | 3 | 35.6 | IIA | 0.99 |  |  | B | Check !! | IIC | Check !! | I | Check !!
1-Pentene | 109-67-1 | D | I | -18 | 275 | 1.5 | 8.7 | 2.4 | 639.7 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
2-Pentene | 109-68-2 | D | I | -18 |  |  |  | 2.4 | [5 empty] | B | Check !! | IIC | Check !! | I | Check !!
2-Pentyl Acetate | 626-38-0 | D | I | 23 |  | 1.1 | 7.5 | 4.5 | [5 empty] | B | Check !! | IIC | Check !! | I | Check !!
Phenylhydrazine | 100-63-0 | D |  | 89 |  |  |  | 3.7 | 0.03 |  |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
Process Gas |  | B | GAS |  | 520 | 4 | 75 | 0.1 |  |  | 0.019 | 0.45 |  | B |  | IIC | Check !! | I | Check !!
Propane | 74-98-6 | D | GAS |  | 450 | 2.1 | 9.5 | 1.6 |  | IIA | 0.25 | 0.82 | 0.97 | D |  | IIA |  | I
1-Propanol | 71-23-8 | D | I | 15 | 413 | 2.2 | 13.7 | 2.1 | 20.7 | IIA |  |  | 0.89 | B | Check !! | IIC | Check !! | I | Check !!
2-Propanol | 67-63-0 | D | I | 12 | 399 | 2 | 12.7 | 2.1 | 45.4 | IIA | 0.65 |  | 1 | B | Check !! | IIC | Check !! | I | Check !!
Propiolactone | 57-57-8 | D |  |  |  | 2.9 |  | 2.5 | 2.2 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Propionaldehyde | 123-38-6 | C | I | -9 | 207 | 2.6 | 17 | 2 | 318.5 | IIB |  |  | 0.86 | B | Check !! | IIC | Check !! | I | Check !!
Propionic Acid | 79-09-04 | D | II | 54 | 466 | 2.9 | 12.1 | 2.5 | 3.7 | IIA |  |  | 1.1 | B | Check !! | IIC | Check !! | II | Check !!
Propionic Anhydride | 1979-09-04 | D |  | 74 | 285 | 1.3 | 9.5 | 4.5 | 1.4 |  |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!
n-Propyl Acetate | 123-62-6 | D | I | 14 | 450 | 1.7 | 8 | 3.5 | 33.4 | IIA |  |  | 1.05 | B | Check !! | IIC | Check !! | I | Check !!
n-Propyl Ether | 109-60-4 | C | I | 21 | 215 | 1.3 | 7 | 3.5 | 62.3 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Propyl Nitrate | 627-13-4 | B | I | 20 | 175 | 2 | 100 | [6 empty] | B |  | IIC | Check !! | I | Check !!
Propylene | 115-07-1 | D | GAS |  | 460 | 2.4 | 10.3 | 1.5 |  | IIA | 0.28 |  | 0.91 | B | Check !! | IIC | Check !! | I | Check !!
Propylene Dichloride | 78-87-5 | D | I | 16 | 557 | 3.4 | 14.5 | 3.9 | 51.7 | IIA |  |  | 1.32 | B | Check !! | IIC | Check !! | I | Check !!
Propylene Oxide | 75-56-9 | B,C | I | -37 | 449 | 2.3 | 36 | 2 | 534.4 | IIB | 0.13 |  | 0.7 | B | Check !! | IIC | Check !! | I | Check !!
Pyridine | 110-86-1 | D | I | 20 | 482 | 1.8 | 12.4 | 2.7 | 20.8 | IIA |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Styrene | 100-42-5 | D | I | 31 | 490 | 0.9 | 6.8 | 3.6 | 6.1 | IIA |  | 1.21 |  | B | Check !! | IIC | Check !! | I | Check !!
Tetrahydrofuran | 109-99-9 | C | I | -14 | 321 | 2 | 11.8 | 2.5 | 161.6 | IIB | 0.54 |  | 0.87 | B | Check !! | IIC | Check !! | I | Check !!
Tetrahydronaphthalene | 119-64-2 | D | IIIA |  | 385 | 0.8 | 5 | 4.6 | 0.4 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Tetramethyl Lead | 75-74-1 | C | II | 38 | 9.2 | [8 empty] | B | Check !! | IIC | Check !! | II | Check !!
Toluene | 108-88-3 | D | I | 4 | 480 | 1.1 | 7.1 | 3.1 | 28.53 | IIA | 0.24 |  |  | B | Check !! | IIC | Check !! | I | Check !!
n-Tridecene | 2437-56-1 | D | IIIA |  |  | 0.6 |  | 6.4 | 593.4 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
Triethylamine | 121-44-8 | C | I | -9 | 249 | 1.2 | 8 | 3.5 | 68.5 | IIA | 0.75 |  | 1.05 | B | Check !! | IIC | Check !! | I | Check !!
Triethylbenzene | 25340-18-5 | D |  | 83 |  |  | 56 | 5.6 | [5 empty] | B | Check !! | IIC | Check !! | IIIA | Check !!
2,2,3-Trimethylbutane |  | D |  |  | 442 | [8 empty] | B | Check !! | IIC | Check !! | I | Check !!
2,2,4-Trimethylbutane |  | D |  |  | 407 | [8 empty] | B | Check !! | IIC | Check !! | I | Check !!
2,2,3-Trimethylpentane |  | D |  |  | 396 | [8 empty] | B | Check !! | IIC | Check !! | I | Check !!
2,2,4-Trimethylpentane |  | D |  |  | 415 |  |  |  |  | IIA |  |  | 1.04 | B | Check !! | IIC | Check !! | I | Check !!
2,3,3-Trimethylpentane |  | D |  |  | 425 | [8 empty] | B | Check !! | IIC | Check !! | I | Check !!
Tripropylamine | 102-69-2 | D | II | 41 |  |  |  | 4.9 | 1.5 | IIA |  |  | 1.13 | B | Check !! | IIC | Check !! | II | Check !!
Turpentine | 8006-64-2 | D | I | 35 | 253 | 0.8 |  |  | 4.8 |  |  |  |  | B | Check !! | IIC | Check !! | I | Check !!
n-Undecene | 28761-27-5 | D | IIIA |  |  | 0.7 |  | 5.5 | [5 empty] | B | Check !! | IIC | Check !! | I | Check !!
Unsymmetrical Dimethyl Hydrazine | 57-14-7 | C | I | -15 | 249 | 2 | 95 | 1.9 |  | IIB |  |  | 0.85 | B | Check !! | IIC | Check !! | I | Check !!
Valeraldehyde | 110-62-3 | C | I | 280 | 222 |  |  | 3 | 34.3 |  |  |  |  | B | Check !! | IIC | Check !! | IIIB | Check !!
Vinyl Acetate | 108-05-4 | D | I | -6 | 402 | 2.6 | 13.4 | 3 | 113.4 | IIA | 0.7 |  | 0.94 | B | Check !! | IIC | Check !! | I | Check !!
Vinyl Chloride | 1975-01-04 | D | GAS | -78 | 472 | 3.6 | 33 | 2.2 |  | IIA |  |  | 0.96 | B | Check !! | IIC | Check !! | I | Check !!
Vinyl Toluene | 25013-15-4 | D |  | 52 | 494 | 0.8 | 11 | 4.1 | [5 empty] | B | Check !! | IIC | Check !! | II | Check !!
Vinylidene Chloride | 75-35-4 | D | I |  | 570 | 6.5 | 15.5 | 3.4 | 599.4 | IIA |  |  | 3.91 | B | Check !! | IIC | Check !! | I | Check !!
Xylene | 1330-20-7 | D | I | 25 | 464 | 0.9 | 7 | 3.7 |  | IIA | 0.2 |  | 1.09 | B | Check !! | IIC | Check !! | I | Check !!
Xylidine | 121-69-7 | C | IIIA | 63 | 371 | 1 |  | 4.2 | 0.7 |  |  |  |  | B | Check !! | IIC | Check !! | IIIA | Check !!

## 표지
HAZARDOUS SOURCE / SUBSTANCE LIST
(PROCESS DEPARTMENT)
Project Name : XXXX project
Job No. : SC-XXXX
| REV. | DATE | WRITTEN BY | CHECKED BY | APPROVED BY
| A | 2019.01.02.

## Source
|  |  |  | HAZARDOUS SOURCE LIST | [8 empty] | Temp. Class
[13 empty] | EU IEC / US NEC 505 |  | US NEC 500
Project Name : | [11 empty] | REVISION STATUS: 0 |  | AIT (℃) |  | AIT (℃)
Job No. : | [12 empty] | T1 | 450 이상 | T1 | 450 이상
[13 empty] | T2 | 300 이상 | T2 | 300 이상
MATERIAL DESCRIPTION | FORMULA | M.WT | MATERIAL PROPERTIES | [8 empty] | REMARKS |  |  | T2A | 280 이상
|  |  | FLASH POINT | VAPOR DENSITY | AUTO IGNITION TEMP | BOILING POINT | VAPOR PRESSURE | LFL | UFL | Temp. Class | Gas Group |  |  |  | T2B | 260 이상
|  |  | 0C | AIR=1 | 0C | 0C | mmHg | %V/V | %V/V | [5 empty] | T2C | 230 이상
Methane | CH4 | 16.04 | Flammable, -233 | 0.6 | 600 | -161.49 | - | 5 | 15 | T1 | IIA |  |  |  | T2D | 215 이상
Ethane | C2H6 | 30.07 | -29 | 1 | 472 | -88.6 | - | 3 | 12.5 | T1 | IIA |  | T3 | 200 이상 | T3 | 200 이상
Propane | C3H8 | 44.1 | Flammable, -104.0 | 1.6 | 450 | -42.04 | - | 2.1 | 9.5 | T1 | IIA |  |  |  | T3A | 180 이상
Isobutane | C4H10 | 58.12 | Flammable, -84.4 | 2 | 460 | -11.72 | - | 1.8 | 8.4 | T1 | IIA |  |  |  | T3B | 165 이상
n-Butane | C4H10 | 58.12 | -60 | 2 | 288 | -0.5 | - | 1.9 | 8.5 | T3 | IIA |  |  |  | T3C | 160 이상
Isopentane | C5H12 | 72.15 | -57.2 | - | 420 | 27.84 | 688.6 | - | - | T2 | - |  | T4 | 135 이상 | T4 | 135 이상
n-Pentane | C5H12 | 72.15 | -40 | 2.5 | 243 | 36.07 | 513 | 1.5 | 7.8 | T3 | IIA |  |  |  | T4A | 120 이상
n-Hexane | C6H14 | 86.18 | -23 | 3 | 225 | 68.73 | 152 | 1.1 | 7.5 | T3 | IIA |  | T5 | 100 이상 | T5 | 100 이상
n-Heptane | C7H16 | 100.2 | -4 | 3.5 | 204 | 98.43 | 45.5 | 1 | 6.7 | T3 | IIA |  | T6 | 85 이상 | T6 | 85 이상
n-Octane | C8H18 | 114.23 | 13 | 3.9 | 206 | 125.68 | 14 | 1 | 6.5 | T3 | IIA
n-Nonane | C9H20 | 128.26 | 31 | 4.4 | 205 | 150.82 | 4.4 | 0.8 | 2.9 | T3 | IIA |  | Gas Group (Refer to NFPA 497, Table 4.4.2.)
Hydrogen Sulfide | H2S | 34.08 | Flammable, -82.4 | 1.2 | 260 | -60.35 | - | 4 | 44 | T3 | IIB |  | Group | Classification
Triethylene Glycol | C6H14O2 | 150.2 | 177 | 5.17 | 371 | 286 |  | 0.9 | 9.2 | T2 | IIB | Refer TGAS | ⅡA | Atmospheres containing acetone, ammonia, ethyl alcohol, gasoline, methane, propane, or flammable gas, flammable liquid produced vapor, or combustible liquid produced vapor mixed with air that may burn or explode, having either a maximum experimental safe gap (MESG) value greater than 0.90 mm or minimum igniting current ratio (MIC ratio) greater than 0.80.
Ethylene Glycol | C2H6O2 | 62.07 | 111 | 2.14 | 398 | 197.6 |  | 3.2 | 22 | T2 | IIB | Refer MSDS
Methyl Diethanolamine (MDEAmine) | CH5H13NO3 | 119.16 | 137 | 1.04 | 265 | 243 | 0.01 | 0.9 | 8.4 | T2 | - | Refer MSDS
Benzene | C6H6 | 78.11 | -11 | 2.8 | 498 | 80.1 | 94.8 | 1.2 | 7.8 | T1 | IIA
Toluene | C7H8 | 92.14 | 4 | 3.1 | 480 | 110.6 | 28.53 | 1.1 | 7.1 | T1 | IIA |  | ⅡB | Atmospheres containing acetaldehyde, ethylene, or flammable gas, flammable liquid produced vapor, or combustible liquid produced vapor mixed with air that may burn or explode, having either maximum experimental safe gap (MESG) values greater than 0.50 mm and less than or equal to 0.90 mm or minimum igniting current ratio (MIC ratio) greater than 0.45 and less than or equal to 0.80.
Ethyl Benzene | C8H10 | 106.17 | 15 | 3.7 | 432 | 136 | 9.6 | 0.8 | 6.7 | T2 | -
Xylene | C8H10 | 106.16 | 25 | 3.7 | 464 | 139 | - | 0.9 | 7 | T1 | IIA
Methyl Mercaptan | CH4S | 48.11 | -18 | 1.7 | - | 6 | - | 3.9 | 21.8 |  | - |  | ⅡC | Atmospheres containing acetylene, hydrogen, or flammable gas, flammable liquid-produced vapor, or combustible liquid produced vapor mixed with air that may burn or explode, having either a maximum experimental safe gap (MESG) value less than or equal to 0.50 mm or minimum igniting current ratio (MIC ratio) less than or equal to 0.45.
Ethyl Mercaptan | C₂H₆S | 62.13 | ?18 | 2.1 | 300 | 35 | 527.4 | 2.8 | 18 | T3 | IIB
Carbon Disulfide | CS2 | 76.139 | -30 | 2.6 | 90 | 46.3 | 358.8 | 1.3 | 50 | T6 | IIC
|  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A |  | #N/A
Ammonia | NH3 | 17.03 | - | 0.6 | 651 | -33.5 | 7498 | 15 | 28 | T1 | IIA
Hydrogen | H2 | 2 | - | 0.1 | 500 |  | - | 4 | 75 | T1 | IIC
Ethylene Glycol | C2H6O2 | 62.07 | 47 | 4.7 | 379 | 197.6 |  | 1.7 | 15.3 | T2 | IIB | Refer TGAS
Note on E9: STE: refer to TGAS project
Note on E11: STE: refer to TGAS project
Note on E12: STE: refer to TGAS project
Note on E20: STE: refer to TGAS project
Note on E21: STE: refer to TGAS project May Be combustible at higher temperature
Note on K22: STE: infromation refer to https://en.wikipedia.org/wiki/Flammability_limit
Note on B27: STE: p-Xylene+m-Xylene+o-Xylene

## Vessel,Tank
HAZARDOUS SUBSTANCE LIST
필요 | Project Name : | [26 empty] | REVISION STATUS: 0
Job No. :
| Equipment No. | Service | Substance (Note 1) |  | Volume of |  | State (V/L) | Flash Point (0C) (Note 1) | Auto ignition Temp (0C) (Note 1) | Boiling Point (0C) (If required) | Vapour Density (AIR = 1) | Operating Conditon |  | For Liquids |  |  |  | For Vapors |  |  | Combustible (Y/N) (Note 2) | Flammable (Y/N) (Note 3) | Toxic (Y/N) (Note 4) | Fire Potential Equipment (Y/N) | Toxic Gas Detector (Y/N) | Flammable gas Detector (Y/N) | Selected Case | Remarks
[14 empty] | Liquid Volume (m3) | Liquid Flow Rate (m3/hr) | Holding a Liquid volume of 4m3 or more, of butane or light products | Liquid Volume> 2 m3 or Liquid Flow >5m3/hr | Vapor Volume (Kg) | Vapor Flow Rate (Kg/hr) | Vapor Volume > 6000Kg or Vapor Flow >4500Kg/hr
|  |  | Component | (mol%) | H2S | H2 | [5 empty] | Press. (barG) | Temp. (0C)
| [Eq_common] 에 Itemno 값 | [Eq_common] 에 ServiceName 값 | [usersetting_Component] component 이름을 세로로 모두 나열 (조건) 1. [usersetting_Component] 에서 Formula 가 none 인것 제외 2. 해당 심볼에 연결된 들어오는 방향의 streamno --> [HMB_composition] 중 COMP1~60의 값이 0인 COMP 제외 | 좌측에 선정된 COMP 들의 [HMB_composition] 값들을 세로로 모두 나열 |  |  | 해당 심볼에 연결된 들어오는 방향의 stream no --> [HMB_condition] 의 streamphase 값을 약자로 입력 Vapor -> V Liquid -> L Vapor+Liquid -> V+L |  |  |  |  | [Eq_pressurized] 에 OperatingPressureUpper & / & [Eq_pressurized] 에 OperatingPressureLower (조건) [Eq_pressurized] 에 OperatingPressureLower가 공백이면 / 는 필요없음 | [Eq_pressurized] 에 OperatingTemperatureUpper & / & [Eq_pressurized] 에 OperatingTemperatureLower (조건) [Eq_pressurized] 에 OperatingtemperatureLower가 공백이면 / 는 필요없음
예시
| C-1001 | Gas Mercury Removal Bed | Methane Ethane Propane C4+ H2S | 83.47 1.75 0.8 1.8 0.76 |  |  | V |  |  |  |  | 3.0 / -1.0 | 200
Note: 1) LFL 이상 mol%의 Single component 중 가장 낮은 flash point로 작성
2) Combustible fluid definition : (Project 기준 작성)
3) Flammable fluid definition : (Project 기준 작성)
4) Toxic : [H2S concentration] Gas/vapour : 0.1 %(v/v) or non-gaseous : 0.06 %(w/w)
PAP 심볼 타입이
Column / Drum / Tank 인것들을 대상으로
Note on T10: STE: no information of dimension

## Comp
HAZARDOUS SUBSTANCE LIST
필요 | Project Name : |  | Shell OGP FEED | [23 empty] | REVISION STATUS: 0
| Job No. : | SG6609
| Equipment No. | Service | Substance (Note 1) |  | Volume of |  | State (V/L) | Flash Point (0C) (Note 1) | Auto ignition Temp (0C) (Note 1) | Boiling Point (0C) (If required) | Vapour Density (AIR = 1) | Operating Conditon |  | For Liquids |  |  | For Vapors |  |  | Combustible (Y/N) (Note 2) | Flammable (Y/N) (Note 3) | Toxic (Y/N) (Note 4) | Fire Potential Equipment (Y/N) | Toxic Gas Detector (Y/N) | Flammable gas Detector (Y/N) | Selected Case | Remarks
[14 empty] | Liquid Volume (m3) | Liquid Flow Rate (m3/hr) | Liquid Volume> 2 m3 or Liquid Flow >5m3/hr | Vapor Volume (Kg) | Vapor Flow Rate (Kg/hr) | Vapor Volume > 6000Kg or Vapor Flow >4500Kg/hr
|  |  | Component | (mol%) | H2S | H2 | [5 empty] | Press. (barG) | Temp. (0C)
| 동일 | 동일 | 동일 | 동일 | 동일 | 동일 | 동일 |  |  |  |  | 동일 | 동일
Note: 1) LFL 이상 mol%의 Single component 중 가장 낮은 flash point로 작성
2) Combustible fluid definition : (Project 기준 작성)
3) Flammable fluid definition : (Project 기준 작성)
4) Toxic : [H2S concentration] Gas/vapour : 0.1 %(v/v) or non-gaseous : 0.06 %(w/w)
PAP 심볼 타입이
Compressor 인것들을 대상으로
Note on S10: STE: Vendor information
Note on N11: STE: Equipment list
Note on O11: STE: Equipment list
Note on S11: STE: Vendor information
Note on N12: STE: Equipment list
Note on O12: STE: Equipment list
Note on S12: STE: Vendor information

## Filter
HAZARDOUS SUBSTANCE LIST
필요 | Project Name : |  | Shell OGP FEED | [24 empty] | REVISION STATUS: 0
| Job No. : | SG6609
| Equipment No. | Service | Substance (Note 1) |  | Volume of |  | State (V/L) | Flash Point (0C) (Note 1) | Auto ignition Temp (0C) (Note 1) | Boiling Point (0C) (If required) | Vapour Density (AIR = 1) | Operating Conditon |  | For Liquids |  |  |  | For Vapors |  |  | Combustible (Y/N) (Note 2) | Flammable (Y/N) (Note 3) | Toxic (Y/N) (Note 4) | Fire Potential Equipment (Y/N) | Toxic Gas Detector (Y/N) | Flammable gas Detector (Y/N) | Selected Case | Remarks
[14 empty] | Liquid Volume (m3) | Liquid Flow Rate (m3/hr) | Holding a Liquid volume of 4m3 or more, of butane or light products | Liquid Volume> 2 m3 or Liquid Flow >5m3/hr | Vapor Volume (Kg) | Vapor Flow Rate (Kg/hr) | Vapor Volume > 6000Kg or Vapor Flow >4500Kg/hr
|  |  | Component | (mol%) | H2S | H2 | [5 empty] | Press. (barG) | Temp. (0C)
| 동일 | 동일 | 동일 | 동일 | 동일 | 동일 | 동일 |  |  |  |  | 동일 | 동일
Note: 1) LFL 이상 mol%의 Single component 중 가장 낮은 flash point로 작성
2) Combustible fluid definition : (Project 기준 작성)
3) Flammable fluid definition : (Project 기준 작성)
4) Toxic : [H2S concentration] Gas/vapour : 0.1 %(v/v) or non-gaseous : 0.06 %(w/w)
PAP 심볼 타입이
Filter 인것들을 대상으로

## Package
HAZARDOUS SUBSTANCE LIST
필요 | Project Name : |  | Shell OGP FEED | [24 empty] | REVISION STATUS: 0
| Job No. : | SG6609
| Equipment No. | Service | Substance (Note 1) |  | Volume of |  | State (V/L) | Flash Point (0C) (Note 1) | Auto ignition Temp (0C) (Note 1) | Boiling Point (0C) (If required) | Vapour Density (AIR = 1) | Operating Conditon |  | For Liquids |  |  |  | For Vapors |  |  | Combustible (Y/N) (Note 2) | Flammable (Y/N) (Note 3) | Toxic (Y/N) (Note 4) | Fire Potential Equipment (Y/N) | Toxic Gas Detector (Y/N) | Flammable gas Detector (Y/N) | Selected Case | Remarks
[14 empty] | Liquid Volume (m3) | Liquid Flow Rate (m3/hr) | Holding a Liquid volume of 4m3 or more, of butane or light products | Liquid Volume> 2 m3 or Liquid Flow >5m3/hr | Vapor Volume (Kg) | Vapor Flow Rate (Kg/hr) | Vapor Volume > 6000Kg or Vapor Flow >4500Kg/hr
|  |  | Component | (mol%) | H2S | H2 | [5 empty] | Press. (barG) | Temp. (0C)
| 동일 | 동일 | 동일 | 동일 | 동일 | 동일 | 동일 |  |  |  |  | 동일 | 동일
Note: 1) LFL 이상 mol%의 Single component 중 가장 낮은 flash point로 작성
2) Combustible fluid definition : (Project 기준 작성)
3) Flammable fluid definition : (Project 기준 작성)
4) Toxic : [H2S concentration] Gas/vapour : 0.1 %(v/v) or non-gaseous : 0.06 %(w/w)
PAP 심볼 타입이
Miscellaneous 인것들을 대상으로

## Pump
HAZARDOUS SUBSTANCE LIST
필요 | Project Name : |  | Shell OGP FEED | [23 empty] | REVISION STATUS: 0
| Job No. : | SG6609
| Equipment No. | Service | Substance (Note 1) |  | Volume of |  | State (V/L) | Flash Point (0C) (Note 1) | Auto ignition Temp (0C) (Note 1) | Boiling Point (0C) (If required) | Vapour Density (AIR = 1) | Operating Conditon |  | For Liquids |  |  | For Vapors |  |  | Combustible (Y/N) (Note 2) | Flammable (Y/N) (Note 3) | Toxic (Y/N) (Note 4) | Fire Potential Equipment (Y/N) | Toxic Gas Detector (Y/N) | Flammable gas Detector (Y/N) | Selected Case | Remarks
[14 empty] | Liquid Volume (m3) | Liquid Flow Rate (m3/hr) | LNG/LPG | Vapor Volume (Kg) | Vapor Flow Rate (Kg/hr) | Vapor Volume > 6000Kg or Vapor Flow >4500Kg/hr
|  |  | Component | (mol%) | H2S | H2 | [5 empty] | Press. (barG) | Temp. (0C)
| 동일 | 동일 | 동일 | 동일 |  |  | 동일 |  |  |  |  | 동일 | 동일
Note: 1) LFL 이상 mol%의 Single component 중 가장 낮은 flash point로 작성
2) Combustible fluid definition : (Project 기준 작성)
3) Flammable fluid definition : (Project 기준 작성)
4) Toxic : [H2S concentration] Gas/vapour : 0.1 %(v/v) or non-gaseous : 0.06 %(w/w)
PAP 심볼 타입이
centrifugal / metering / submerged pump인것들을 대상으로

## HeatEx
HAZARDOUS SUBSTANCE LIST
필요 | Project Name : |  | Shell OGP FEED | [24 empty] | REVISION STATUS: 0
| Job No. : | SG6609
| Equipment No. | Service | Substance (Note 1) |  | Volume of |  | State (V/L) | Flash Point (0C) (Note 1) | Auto ignition Temp (0C) (Note 1) | Boiling Point (0C) (If required) | Vapour Density (AIR = 1) | Operating Conditon |  | For Liquids |  |  |  | For Vapors |  |  | Combustible (Y/N) (Note 2) | Flammable (Y/N) (Note 3) | Toxic (Y/N) (Note 4) | Fire Potential Equipment (Y/N) | Toxic Gas Detector (Y/N) | Flammable gas Detector (Y/N) | Selected Case | Remarks
[14 empty] | Liquid Volume (m3) | Liquid Flow Rate (m3/hr) | Holding a Liquid volume of 4m3 or more, of butane or light products | Liquid Volume> 2 m3 or Liquid Flow >5m3/hr | Vapor Volume (Kg) | Vapor Flow Rate (Kg/hr) | Vapor Volume > 6000Kg or Vapor Flow >4500Kg/hr
|  |  | Component | (mol%) | H2S | H2 | [5 empty] | Press. (barG) | Temp. (0C)
| 동일 | 동일 | 동일 | 동일 |  |  | 동일 |  |  |  |  | 동일 | 동일
Note: 1) LFL 이상 mol%의 Single component 중 가장 낮은 flash point로 작성
2) Combustible fluid definition : (Project 기준 작성)
3) Flammable fluid definition : (Project 기준 작성)
4) Toxic : [H2S concentration] Gas/vapour : 0.1 %(v/v) or non-gaseous : 0.06 %(w/w)
PAP 심볼 타입이
air fin cooler / heat exchanger 인것들을 대상으로

## Other
HAZARDOUS SUBSTANCE LIST
필요 | Project Name : |  | Shell OGP FEED | [24 empty] | REVISION STATUS: 0
| Job No. : | SG6609
| Equipment No. | Service | Substance (Note 1) |  | Volume of |  | State (V/L) | Flash Point (0C) (Note 1) | Auto ignition Temp (0C) (Note 1) | Boiling Point (0C) (If required) | Vapour Density (AIR = 1) | Operating Conditon |  | For Liquids |  |  |  | For Vapors |  |  | Combustible (Y/N) (Note 2) | Flammable (Y/N) (Note 3) | Toxic (Y/N) (Note 4) | Fire Potential Equipment (Y/N) | Toxic Gas Detector (Y/N) | Flammable gas Detector (Y/N) | Selected Case | Remarks
[14 empty] | Liquid Volume (m3) | Liquid Flow Rate (m3/hr) | Holding a Liquid volume of 4m3 or more, of butane or light products | Liquid Volume> 2 m3 or Liquid Flow >5m3/hr | Vapor Volume (Kg) | Vapor Flow Rate (Kg/hr) | Vapor Volume > 6000Kg or Vapor Flow >4500Kg/hr
|  |  | Component | (mol%) | H2S | H2 | [5 empty] | Press. (barG) | Temp. (0C)
| 동일 | 동일 | 동일 | 동일 | 동일 | 동일 | 동일 |  |  |  |  | 동일 | 동일
Note: 1) LFL 이상 mol%의 Single component 중 가장 낮은 flash point로 작성
2) Combustible fluid definition : (Project 기준 작성)
3) Flammable fluid definition : (Project 기준 작성)
4) Toxic : [H2S concentration] Gas/vapour : 0.1 %(v/v) or non-gaseous : 0.06 %(w/w)
PAP 심볼 타입이
equipment 중 지금까지 대상아니였던 나머지 것들 모두